## Slide 1
Shift Training:
Detector Control System
Stefan Schlenker, CERN
for ATLAS DCS

## Slide 2
ATLAS DCS Overview
Function & Architecture
Monitor and control detector operation
Total >107 parameters distributed over >130 LCS (rack servers)
Archiving of selected parameters to Oracle database
Interfaced with DAQ/RunControl
Links to external controls systems (LHC, Infrastructure)
Remote access: direct and via web applications
System | Component | # Servers (# Appl.) | # Archived Parameters | Total # Parameters | # FSM Objects
Inner Detector | Pixel | 11(12) | 57k | 1’086k | 9.1k
 | Silicon strips | 11(11) | 106k | 1’265k | 14.7k
 | Transit. radiation | 11(11) | 69k | 123k | 13k
 | Services | 7(8) | 16k | 494k | 3.7k
Calorimeters | Liquid Argon | 13(13) | 27k | 910k | 8.3k
 | Tile | 5(5) | 51k | 719k | 2.4k
Muon Spectrometer | Drift tubes | 29(29) | 214k | 3’229k | 19.2k
 | Cathode strip | 2(2) | 1.3k | 109k | 0.6k
 | Resistive plate | 7(7) | 139k | 1’597k | 2.5k
 | Thin gap | 7(7) | 81k | 1’225k | 10k
 | Services | 2(2) | 0.7k | 55k | 0.04k
Forward detectors |  | 4(4) | 4.9k | 194k | 0.9k
Common Services | Counting rooms | 7(7) | 23k | 568k | 4.7k
 | Trigger & DAQ | 2(2) | 11k | 386k | 1.3k
 | External+safety | 4(6) | 8.0k | 144k | 0.4k
 | Global services | 9(13) | 1.2k | 222k | 0.4k
Total |  | 131(139) | 809k | 12.3M | 91.2k

## Slide 3: Operation in ACR
Interfaces
Finite State Machine (FSM) and Alarm Screens
2
1

## Slide 4
Desk Details
ACR Stations
DCS desk: Global FSM for Control, FSM ownership, global Alarms
Shift Leader desk: Global FSM for Monitoring and LHC interaction (handshake), global Alarms
System Shifter desks: FSM and Alarms for respective system group (ID, CAL, MUON)
Be aware:
All desks: limited # of UIs!! Counts per system, alarm if close to limit
Shifter Desk pc-atlas-cr-*
DCS Desk pc-atlas-cr-dcs
FSM
Alarms
Global FSM
Control
Alarms
LHC FSM

## Slide 5
Alarm Screen
Active and non-acknowledged alarms
Alarm = parameter out of good range
Options for each alarm (right-click):
  Mask alarm on UI level until the alarm condition goes
  Insert alarm to ELOG with comment
  Display trend plot of value
  Alarm help on TWiki
Acknowledgement:
  Only for some alarms
  Operator needs to acknowledge (left-click on “!!!”), otherwise they won’t disappear from screen when resolved
  Unacknowledged, but resolved alarms are shown as „WENT“ with grey color
Summary alert:
  Single alarm entry hiding several alerts of same type (accessible via “Details”)
Filters:
  Different sets of filters exist, e.g. sub-detectors
  Use always “Default” unless you know what you are doing, always revert back

## Slide 6: Finite State Machine (FSM)
State machine hierarchy
  Detector hardware represented by FSM objects, hierarchically structured
State&Command propagation
  State model for devices (ON,OFF,…) and logical objects (READY, NOT_READY,…)
  Propagation upwards (using programmed logic for parent depending on child states)
  Commands propagated downwards
Status
  Error handling upwards
Object operations
  Commands
  Enable/disable (low level )
  Take/release/include/exclude (high level )
  Access control for all operations
User Interface
  Browsing and object operation…
SCADA / PVSS Layer
GCS
SCS 2
SCS N
TTC
N
.
1
LCS
N
.
1
.
1
Dev
N
-
1
LCS
N
.
1
.
2
Dev
N
...
TTC
1
.
N
SCS 1
TTC
1
.
1
TTC
1
.
2
LCS
1
.
1
.
1
LCS
1
.
1
.
2
Sub-sys
1
.
1
.
2
.
1
Sub-sys
1
.
1
.
2
.
2
Dev
1
Dev
2
Dev
4
Dev
3
Dev
5
...
**only mandatory for relevant sub-detectors
STATES,
COMMANDS
STATUS
State machine object
OK
WARNING
ERROR
FATAL
SHUTDOWN
NOT_READY
READY
GOTO_STANDBY
STANDBY**
GOTO_READY
GOTO_STANDBY
GOTO_SHUTDOWN
UNKNOWN
RECOVER
GOTO_ANY
TRANSITION
Shift
Operator
Detector
Expert

## Slide 7
FSM Screen
Operator Control

## Slide 8
  Checkboxes:
  Enabled, Controllable
  Disabled, Controllable
  Enabled, Not controllable (either free or not owned + exclusive sub-tree)
  Disabled, Not controllable
FSM Screen: Partitioning Modes
Padlock background = tree completeness:
  Tree complete
  Excluded children (!)
  Disabled children
 Control:
  No propagation, NO commands
  Propagation (if Included), Commands by you
  Propagation (if Included), Commands by all
  Propagation (if Included), NO commands
  Propagation (if Included), Commands by all
  No propagation, NO commands
  Propagation, NO commands
  Padlocks:
  No control, Free
  Exclusive, Owner
  Shared, Owner
  Exclusive, NOT Owner
  Shared, NOT Owner
  No control, Locked Out
  No control, Included
  High level objects:
  Low level objects:
Change mode with left-click on padlock:
Change mode with left-click on checkbox:

## Slide 9
Access Control
Aim: prevent accidental actions
Username, Password: CERN account
Shifters get DCS:<sub-det>:operator privileges for shift, thus could:
  Mask/acknowledge alarms
  Operate FSM objects:
    Enable/disable
    Take/release/include/exclude (if owner)
    Commands
Please use FSM actions only after request by an expert or if stated explicitly in sub-system instructions!
Shift Leader roles/privileges:
  DCS:<sub-det>:operator for all sub-dets, but not in sub-domains (e.g. LARHV) as fallback solution
  Additionally BIS operator (see Beams training)

## Slide 10
DCS Back-End Monitoring
Monitor state of DCS back-end itself (processes, machines, …)
Accessible on FSM screen
  Global: “DCS BE”
  Sub-det: “XYZ SYSTEMS”
Control over running panels from within ACR, possibility to monitor and kill (emergency only!) user interfaces by shift leaders
Follow up of problems only by DCS experts (sub-detector or central)

## Slide 11
LHC Interaction
Synchronization of DCS with LHC operation and run control
Detector safety requires lower voltage levels during unstable beam conditions (beam injection, adjust, dump) =
State change  automated (atm except IBL/Pixel), synchronization with DAQ run control, should take max. 5 minutes
Audible notifications from DCS for important beam events
Beam backgrounds and luminosity monitored via DCS (LHC FSM tree)
Train Injection
Energy Ramp
Collisions
Stable Beams
Pixel HV
Drift Chamber HV
Beam Energy
Luminosity
Beam Intensity
Stable Flag
READY
STANDBY
STANDBY

## Slide 12
Beam Interaction – Details
Hardware permits vs. Software “safe for beam”
Hardware permits (left widgets) sometime generated via DCS
Software flags (right widgets) evaluate total sub-detector condition independent of FSM configuration
FSM states to x-check consistency
Right-click on widgets to get history (if archived)
Global
Software Flag
SCS
Software Flag
LCS
Software Flag

## Slide 13
Shifter Tasks
Preparation
Check respective system documentation
In particular inform yourself about current problems and solutions, on-call numbers
Shift hand-over
Ask previous shifter about all remaining problems and possibly pending follow up
Check user interfaces to be available and configured, login with your account (FSM & Alarm screens)
During Shifts
Watch Alarm and FSM screen and follow up problems
Check actively with other shifters when suspecting problem cause in other systems,
Inform shift leader about possible impact of DCS problems on data taking efficiency
Report to ELOG:
  Message Type = Default
  System affected:
  DCS + sub-detector
System
assignment
(2015)
Desk | System Identifiers
ID | PIX, SCT, TRT, IDE
CALO+FWD | LAR, TIL, FWD, LCD, ZDC, RPO
MUON | MDT, CSC, RPC, TGC, MUO
DQ | LHC, LUM
SLIMOS | CIC, EXT, SAF, GCS
SHIFT LEADER | TDQ, GCS

## Slide 14
Shifter Tasks: Alarms
Aim: Get / Keep alarm screen empty!
Procedure:
Follow up according to severity
Try to understand alarms, check documentation (= system shifters instructions and right-click alarm help) for specific procedures
If problem cannot be fixed, contact system expert
If alarm condition cannot be removed on short timescale (<~30min), mask alarm in agreement with expert or following specific instructions
If (masked) alarm condition cannot be removed on long timescale (>1week), expert is responsible to deactivate alarm or change alarm limits until problem is solved
Acknowledgeable alarms: acknowledge after informing expert
Report to ELOG what has been done, including details (list of alarms treated!)
WARNING
ERROR
FATAL
Fatal failure, immediate attention required. Call.
Failure condition which might prevent taking good data. Call.
Minor problem. Upcoming failure which might be avoidable. Elog/maybe call.

## Slide 15
Shifter Tasks: FSM
Aim: Get / Keep FSM
Procedure:
Beginning of shift: check for tree being incomplete  no objects should show (excluded sub-trees), in case they do  contact expert
Understand problems (State!=READY, Status!=OK)
  Navigate down to object causing the problem, check on respective panel
  Check documentation for specific procedures
If problem cannot be fixed, contact system expert
If problem cannot be solved on short timescale (<~30min), Disable or Exclude only affected FSM object in agreement with expert or following specific instructions
  Use with caution since this object will not receive global FSM commands nor will report further state/status changes, do not disable all children objects and leave parent enabled
  Note: Exclude/Include can only be done on DCS desk, Disable/Enable on all FSM screens
Interventions on monitored trees should be done by handing over ownership from DCS desk to experts (Exclude), then Include sub-tree when intervention is over and check for tree completeness (= no )
Report to ELOG what has been done, including details (list objects/trees)
OK
READY
STANDBY